|  |  | OEM |
| --- | --- | --- |
|  | Strap-on Temperature Sensors | QAD... |

The strap-on temperature sensor is designed for mounting on pipes to acquire the temperature of the medium inside the pipe

The QAD... and this Data Sheet are intended for OEMs which use the temperature sensors in or on their products

Use

Control and limitation of the flow temperature

Limitation of the return temperature

### Type summary

| Type reference | Sensing element | Measurement range | Tolerance* | Time constant | Weight | Packing size pieces |
| --- | --- | --- | --- | --- | --- | --- |
| QAD21/201 | LG-Ni 1000 ( at 0 °C | -30...130 °C | ±0.4 K | 2 s | 72 g | 45 ** |
| QAD21/209 |  |  |  |  |  | 100 *** |
| QAD36/101 | NTC 10 k( at 25 °C | -30...125 °C | ±0,5 K | 6 s | 0,072 kg | 45 ** |

*	At 0 °C excluding conducting error and self-heating effect, NTC at 25 °C

**	Individually packed in multipacks  /  ***   Multipacks

Ordering

When ordering, please give type reference according to “Type summary“, e.g. QAD21/209

Technical design

The sensing element is a thin-film LG-Ni element with a resistance of 1000 (  at 0 °C or a NTC 10 k( at 25 °C.

Mechanical design

The strap-on sensor consists of plastic housing with snap-on cover. The connection terminals are accessible after removal of the cover. The cable is introduced through a cable entry gland Pg11. A strap is used to mount the sensor on pipes having a diameter of 15 to 50 mm.

### Notes

Planning, mounting and installation

Depending on the application, the sensor should be located as follows:

Flow temperature control:
On the heating flow pipe:
– Immediately after the pump if the pump is installed in the flow
– 1.5…2 m after the mixing valve if the pump is installed in the return

Return temperature limitation:
On the return pipe where the temperature to be limited can be correctly acquired. In any case, the sensor must be installed where the water is well mixed.

The sensor may not be covered by lagging.

Permissible cable lengths

The permissible cable lengths between controller and sensor are the following:

| Cable | Cable dia. | Max. cable length |
| --- | --- | --- |
| Copper cable | 0.6 mm dia. | 5.5 mm | 20 m |
| Copper cable | 1 mm2 | 6.6 mm | 80 m |
| Copper cable | 1.5 mm2 | 7.2 mm | 120 m |

### Technical data

Norms and standards

| Climatic conditions Mechanical conditions | to IEC 721-3 to IEC 721-3 |
| --- | --- |
| Product safety Degree of protection of housing Safety class Insulation resistance Insulation voltage | IP 42 to EN 60 529 III to EN 60 529 >10 M( >500 V |
| Electrical connections Connection terminals Cable entry gland | interchangeable Pg11 |
| Color | RAL 7016 (anthracite) |

### Dimensions

# Text boxes

(2001 Siemens Building Technologies Ltd.

Subject to alteration